## in
PARAMETER | VALUE
MT_FILE_INFO_TYPE | SS
MT_UTILITY_NAME | Central Hudson
MT_COUNTRY | United States of America
MT_STATE | New York
MT_DATE_OF_APPLICABILITY | 2023-01-01
MT_DER_SITE_NAME-APP
MT_DER_OWNER_NAME-APP
MT_POWER_CONVERSION_DEV | INVERTER
MT_NP_NORMAL_OP_CAT-APP | CAT_B
MT_NP_ABNORMAL_OP_CAT-APP | CAT_III
MT_NP_P_MAX-MIN-APP
MT_NP_P_MAX-MAX-APP | 50
MT_NP_AC_V_NOM-APP
MT_CIRCUIT_TOPOLOGY
MT_SERVICE_TYPE
MT_PRIMARY_POWER_SOURCE
MT_APPLICATION_PURPOSE
MT_PRIMARY_MOVER
MT_VARIABLE_GENERATION_TYPE
COMMENT | For PV DER, PV_CURVE_P2 should be the lesser value of 0.2 of Prated or Pmin
AP_LIMIT_ENABLE-SS
AP_LIMIT-SS
ES_PERMIT_SERVICE-SS | ENABLED
ES_V_LOW-SS | 0.917
ES_V_HIGH-SS | 1.05
ES_F_LOW-SS | 59.5
ES_F_HIGH-SS | 60.1
ES_DELAY-SS | 300
ES_RANDOMIZED_DELAY-SS
ES_RAMP_RATE-SS
CONST_PF_MODE_ENABLE-SS | DISABLED
CONST_PF_EXCITATION-SS
CONST_PF-SS
CONST_Q_MODE_ENABLE-SS | DISABLED
CONST_Q-SS
QV_MODE_ENABLE-SS | ENABLED
QV_VREF-SS | 1
QV_VREF_AUTO_MODE-SS | DISABLED
QV_VREF_TIME-SS
QV_CURVE_V2-SS | 0.95
QV_CURVE_Q2-SS | 0
QV_CURVE_V3-SS | 1.03
QV_CURVE_Q3-SS | 0
QV_CURVE_V1-SS | 0.91
QV_CURVE_Q1-SS | 0.44
QV_CURVE_V4-SS | 1.07
QV_CURVE_Q4-SS | -0.44
QV_OLRT-SS | 5
QP_MODE_ENABLE-SS | DISABLED
QP_CURVE_P3_GEN-SS
QP_CURVE_P2_GEN-SS
QP_CURVE_P1_GEN-SS
QP_CURVE_P1_LOAD-SS
QP_CURVE_P2_LOAD-SS
QP_CURVE_P3_LOAD-SS
QP_CURVE_Q3_GEN-SS
QP_CURVE_Q2_GEN-SS
QP_CURVE_Q1_GEN-SS
QP_CURVE_Q1_LOAD-SS
QP_CURVE_Q2_LOAD-SS
QP_CURVE_Q3_LOAD-SS
PV_MODE_ENABLE-SS | DISABLED
PV_CURVE_V1-SS | 1.07
PV_CURVE_P1-SS | 1
PV_CURVE_V2-SS | 1.1
PV_CURVE_P2-SS
PV_OLRT-SS | 10
OV2_TRIP_V-SS | 1.2
OV2_TRIP_T-SS | 0.16
OV1_TRIP_V-SS | 1.1
OV1_TRIP_T-SS | 2
UV1_TRIP_V-SS | 0.88
UV1_TRIP_T-SS | 3
UV2_TRIP_V-SS | 0.5
UV2_TRIP_T-SS | 1.1
OF2_TRIP_F-SS | 62
OF2_TRIP_T-SS | 0.16
OF1_TRIP_F-SS | 61.2
OF1_TRIP_T-SS | 300
UF1_TRIP_F-SS | 58.5
UF1_TRIP_T-SS | 300
UF2_TRIP_F-SS | 56.5
UF2_TRIP_T-SS | 0.16
PF_DBOF-SS | 0.036
PF_DBUF-SS | 0.036
PF_KOF-SS | 0.05
PF_KUF-SS | 0.05
PF_OLRT-SS | 5